FB for driving a motorized Valve without Feedback

| Drei_Punkt_Schritt |  |  |
| --- | --- | --- |
| (Bool) |  | (Bool) |
| EN |  | ENO |
| MV Input (INT) |  | Internal_Stroke_Time (INT) |
| 0,00…100,00% |  | 0,00…300,00 s |
| Full_Stroke_Time (INT) |  | Target_Stroke_Time (INT) |
| 10,0…300,0 s |  | 0,00…300,00 |
| Max_On_Time (INT) |  | Valve_Open (BOOL) |
| 0,1…10,0 s |  | 1 = Opening |
| Min_On_Time (INT) |  | Valve_Close (BOOL) |
| 0,1…10,0 s |  | 1 = Closing |
| Off_Time (INT) |  | Internal_Low_Limit (BOOL) |
| 0,1…10,0 s |  | 1 = At internal Low Limit |
| Deadband (INT) |  | Internal_High_Limit (BOOL) |
| 0,00…100,00 % |  | 1 = At internal High Limit |
| High_Limit (INT) |  |  |
| 0,00…100,00 % |  |  |
| Low_Limit (INT) |  |  |
| 0,00…100,00 % |  |  |
| Auto_Manual (BOOL) |  |  |
| 0=Manual 1=Auto |  |  |
| Manual_Open (BOOL) |  |  |
| 1= Open |  |  |
| Manual_Close (BOOL) |  |  |
| 1= Close |  |  |
| Limit_SW_Up (BOOL) |  |  |
| 1= No Limit (NC) |  |  |
| Limit_SW_Close (BOOL) |  |  |
| 1= No Limit (NC) |  |  |

All Input values are not internal monitored so it is nessecary to put in the values like described.

Max_On_Time>Min_On_Time

High_Limit> Low_Limit if no Limit necessary High_Limit to 100,00 and Low_Limit to 0,00

When the EN Bit is set to on all internal Values are Zero cleared this means the FB Starts at 0,00 s Internal Stroke Time.

The Limit switch inputs are NormalClosed Inputs so if there are no Limit switches mounted at the valve set these bits to 1 before switching from Manual to Auto.

Opening and Closing the Valve Manual is only possible if Auto_Manual Bit is 0

This FB is working with a simulated Feedback from Valve that means that runtime of Valve is calculated as feedback. Output Internal_Stroke_Time is momentary Position of Valve and Target_Stroke_Time is the Target of Valve. Internal Stroke Time is only refreshed by falling edge of Open or Close valve output.

All Input Values are internal calculated in Stroke Time Units.

The Valve_Open and Valve_Close output time depends on deviation of Target Stroke time and  Internal_Stroke_Time. This means if deviation is big, length of output pulse is big too.

This is only a Proportional Function.

If the Valve reaches the positive or negative limit switch the corresponding output is switched off, and the Internal_Stroke_Time is set to the High_Limit or Low_Limit value calculated in stroke time of Valve.

If the value reaches the High_Limit or Low_Limit values without Limit switches the open or close output is going on with pulsing but the calculation of internal stroke time is stopping.

If the Full stroke Time Value is changed while FB is running the internal stroke time is scaled to the new values without moving the valve.