## Slide 1
DC2Wire output of E2A
E2A has DC2W output type in series.
One sensor can be attached to both of NPN, PNP circuit!
Reduction of prox stock item numbers in customer!
Mar. 2005 OEE SenBU KT

## Slide 2
+V
GND
out
+V
GND
+V
GND
out
+V
GND
DC3W NPN
DC3W PNP
DC2W
One sensor for both circuit!!
load
load
load
load
Mar. 2005 OEE SenBU KT

## Slide 3
GND
+V
Residual voltage (at ON state)
Leakage current (at OFF state)
load
=3.0V (2m cable, 100mA)
=0.8mA
Load must be work by “+V” – “Residual voltage”
Load must not be work by “Leakage current”
Check!!
Mar. 2005 OEE SenBU KT

## Slide 4
DC2wire sensor can be monitored the current consumption for detecting the cable break or short condition. Customer can easily detect the trouble of cable wiring in his machine.
In the Automotive Companies this combination (DC2wire + monitoring terminal box) has became standard use.
Cable break detection
-- Monitor the current consumption on 2wire line.
-- In case of normally open type,
-- OFF state: I >0.5mA --> cable break : I=0mA
-- ON state: I >load current (depend on load) --> cable break : I=0mA
So customer can set the criteria as minimum 0.5mA for 2 wires.
DC3wire type is not so easy to detect the current consumption difference on power line. (only small change)
Additionally, OMRON has special Device-Net slave terminal for DC2wire sensors. e.g. DRT2-ID**C (-1), DRT2-ID32SLH (-1), DRT2-MD32SLH (-1)
DC2wire Prox can be connected to these slave terminals directly and detected the cable break automatically. (we need some settings)
Also this slave terminal has useful function for predictive maintenance. This can monitor and memorize the ON-OFF cycles. Customer can analyze the maintenance cycle for sensors easily by this data.
Predictive maintenance by DC2wire E2A

## Slide 5
Sensor cable break detection by DRT2

## Slide 6
Sensor cable short detection by DRT2